## RDS
[12 empty] | Season |  | Temperature |  | RH
[14 empty] | Dry Bulb F | Wet Bulb F
Outside Environment Condition
[12 empty] | Summer |  | 110 | 78 | 24
[12 empty] | Monsoon |  | 95 | 82 | 75
[12 empty] | Winter |  | 50 | 46 | 60
[52 empty] | 375X375 | 300X300 |  | 375X375 | 300X300
SR. | AHU | ROOM | ROOM | ROOM DIMENSION | [6 empty] | AREA |  | VOL. | TEMP. | RH | ROOM PRESSURE | CLASS | OCC | EQPT DISSIPATED | LIGHTING LOAD | STEAM | MINIMUM | MINIMUM SUPPLY AIR | FILTERNATION LEVEL FOR AHU |  |  |  | TERMINAL DETAIL | DEHUMIDIFIED AIR QTY | SELECTED SUPPLY | FA | INFILT | EXFILT | PROCESS EXHAUST | INLINE EXHAUST | RETURN AIR | BLEED AIR | COOLING COIL | HEATING | CALCULATED AHU | COOLING | HEATING | CHW | HW | HEPA FILTER |  |  | RETURN AIR RISER |  |  | SUPPLY DIFFUSER |  |  | RETURN DIFFUSER |  |  | SUPPLY GRILL |  |  | RETURN GRILL
|  |  |  | LENGTH |  | WIDTH |  | HEIGHT | [5 empty] | NMT | NMT | [29 empty] | H1 | H2 | H3 | R1-900 | R3-750 | R2-600 | SD1 | SD2 | SD4 | RD1 | RD2 | RD4 | SG1 | SG2 | SG3 | RG1 | RG2 | RG3
NO. | NO | NO. | NAME | MTR | MM | MTR | MM | MTR | MM | FT | M2 | FT2 | FT3 | DEG. F | % | PA | At rest | NOS | KW | WATT PER SQFT |  | ACPH | CFM | FRESH AIR | BLEED FILTER | PRE FILTER | FINE FILTER | ROOM TERMINAL | CFM | CFM | CFM | CFM | CFM | CFM | CFM | CFM | CFM | CHW/DX | HW /HEATER | CFM | TR | KW | USGPM | USGPM | 1000 | 560 | 250 | 600 | 490 | 380 | 1150 | 650 | 300 | 1150 | 650 | 300 | 1700 | 1000 | 500 | 1700 | 1000 | 500
1 | AHU-01 |  | Oointment mfg room | 8.45 | 8450 | 3.75 | 3750 | 3.5 | 3500 | 11.4829 | 31.6875 | 340.9575 | 3915.1944 | 77 | 55 | 20 | D | 2 | 15 | 1.2 | 2 | 30 | 1957.096 | EU-4 | NA | EU-4 | EU-7 | HEPA | 2956.9786 | 2956.9786 | 65.2365 | 132 | 132 | 0 | 0 | 2956.9786 |  | DX | HEATER |  | 5.8979 | 3.1244 |  |  | 4 |  |  |  | 6
2 | AHU-01 |  | Ointment holding room | 2.7 | 2700 | 3.75 | 3750 | 3 | 3000 | 9.8425 | 10.125 | 108.945 | 1072.2933 | 77 | 55 | 30 | D | 1 | 5 | 1.2 | 0 | 30 | 536.0094 | EU-4 | NA | EU-4 | EU-7 | HEPA | 979.7127 | 979.7127 | 17.867 | 132 |  | 0 | 0 | 1111.7127 |  | DX | HEATER |  | 1.9511 | 0.91442 |  |  |  | 2 |  |  |  | 3
[23 empty] | 2493.1054 | [5 empty] | 3936.6913 | 3936.6913 | 83.1035 | 264 | 132 | 0 | 0 | 4068.6913 | 215.1035 |  |  | 4500 | 7.849 | 4.0389
3 | AHU-02 |  | Ointment fillling room | 3.5 | 3500 | 6.2 | 6200 | 3 | 3000 | 9.8425 | 21.7 | 233.492 | 2298.1496 | 77 | 55 | 20 | D | 2 | 5 | 1.2 | 0 | 30 | 1148.7806 | EU-4 | NA | EU-4 | EU-7 | HEPA | 1155.5754 | 1155.5754 | 368.2927 | 132 | 500 | 0 | 0 | 787.5754 |  | DX | HEATER |  | 2.3929 | 1.9598 |  |  | 2 |  |  |  | 4
[23 empty] | 1148.7806 | [5 empty] | 1155.5754 | 1155.5754 | 368.2927 | 132 | 500 | 0 | 0 | 787.5754 | 0.29269 |  |  | 1700 | 2.3929 | 1.9598
4 | AHU-04 |  | Airlock -1 | 2 | 2000 | 1.7 | 1700 | 2.5 | 2500 | 8.2021 | 3.4 | 36.584 | 300.0656 | 77 | 55 | 10 | D | 1 | 0 | 1.2 | 0 | 30 | 149.9944 | EU-4 | NA | EU-4 | EU-7 | HEPA | 81.0416 | 149.9944 | 30 | 106 | 106 | 0 | 0 | 149.9944 |  | DX | HEATER |  | 0.24228 | 0.56071 |  |  |  |  | 1 |  |  | 1
5 | AHU-04 |  | Airlock -2 | 2 | 2000 | 2 | 2000 | 2.5 | 2500 | 8.2021 | 4 | 43.04 | 353.0184 | 77 | 55 | 20 | D | 1 | 0 | 1.2 | 0 | 30 | 176.464 | EU-4 | NA | EU-4 | EU-7 | HEPA | 87.2518 | 176.464 | 30 | 106 | 106 | 0 | 0 | 176.464 |  | DX | HEATER |  | 0.25401 | 0.58506 |  |  |  |  | 1 |  |  | 1
6 | AHU-04 |  | Corridor -1 | 8.2 | 8200 | 2 | 2000 | 2.5 | 2500 | 8.2021 | 16.4 | 176.464 | 1447.3753 | 77 | 55 | 30 | D | 1 | 0 | 1.2 | 0 | 30 | 723.5024 | EU-4 | NA | EU-4 | EU-7 | HEPA | 232.7467 | 723.5024 | 30 | 115 | 591 | 0 | 0 | 247.5024 |  | DX | HEATER |  | 0.56313 | 1.3452 |  |  |  | 2 |  |  | 2
7 | AHU-04 |  | Corridor -2 | 3.3 | 3300 | 1.55 | 1550 | 2.5 | 2500 | 8.2021 | 5.115 | 55.0374 | 451.4222 | 77 | 55 | 30 | D | 1 | 0 | 1.2 | 0 | 30 | 225.6533 | EU-4 | NA | EU-4 | EU-7 | HEPA | 98.7925 | 225.6533 | 30 | 0 | 0 | 0 | 0 | 225.6533 |  | DX | HEATER |  | 0.27582 | 0.63031 |  |  |  | 2 |  |  | 2
8 | AHU-04 |  | IPQC /Change part room | 1.5 | 1500 | 3 | 3000 | 2.5 | 2500 | 8.2021 | 4.5 | 48.42 | 397.1457 | 77 | 55 | 20 | D | 1 | 0 | 1.2 | 0 | 30 | 198.522 | EU-4 | NA | EU-4 | EU-7 | HEPA | 92.427 | 198.522 | 30 | 0 | 0 | 0 | 0 | 198.522 |  | DX | HEATER |  | 0.26379 | 0.60535 |  |  |  |  | 1 |  |  | 1
9 | AHU-04 |  | Material transfer Airlock | 2.2 | 2200 | 2 | 2000 | 2.5 | 2500 | 8.2021 | 4.4 | 47.344 | 388.3202 | 77 | 55 | 20 | D | 1 | 0 | 1.2 | 0 | 25 | 161.7587 | EU-4 | NA | EU-4 | EU-7 | HEPA | 91.392 | 161.7587 | 30 | 0 | 160 | 0 | 0 | 1.7587 |  | DX | HEATER |  | 0.26184 | 0.6013 |  |  |  |  | 1 |  |  | 1
10 | AHU-04 |  | Decartoning room | 2.2 | 2200 | 2 | 2000 | 2.5 | 2500 | 8.2021 | 4.4 | 47.344 | 388.3202 | 77 | 55 | 10 | D | 1 | 0 | 1.2 | 0 | 30 | 194.1104 | EU-4 | NA | EU-4 | EU-7 | HEPA | 91.392 | 194.1104 | 30 | 0 | 160 | 0 | 0 | 34.1104 |  | DX | HEATER |  | 0.26184 | 0.6013 |  |  |  |  | 1 |  |  | 1
[23 empty] | 1830.0052 | [5 empty] | 775.0436 | 1830.0052 | 796 |  |  |  |  | 1034.0052 | 0 |  |  | 2500 | 2.1227 | 4.9292
11 | AHU-03 |  | Airlock | 1.2 | 1200 | 2.25 | 2250 | 2.5 | 2500 | 8.2021 | 2.7 | 29.052 | 238.2874 | 77 | 55 | 20 | D | 1 | 0 | 1.2 | 0 | 30 | 119.1132 | EU-4 | NA | EU-4 | EU-7 | HEPA | 73.7963 | 119.1132 | 15 | 106 | 106 | 0 | 0 | 119.1132 |  | DX | HEATER |  | 0.22859 | 0.53231 |  |  |  |  | 1 |  |  | 1
12 | AHU-03 |  | Unclean Utensil | 1.75 | 1750 | 3 | 3000 | 2.5 | 2500 | 8.2021 | 5.25 | 56.49 | 463.3366 | 77 | 55 | 20 | D | 1 | 0 | 1.2 | 0 | 30 | 231.609 | EU-4 | NA | EU-4 | EU-7 | HEPA | 100.1898 | 231.609 | 15 | 115 | 115 | 0 | 0 | 231.609 |  | DX | HEATER |  | 0.27846 | 0.63579 |  |  |  |  | 1 |  |  | 1
13 | AHU-03 |  | Washing & Drying area | 4.1 | 4100 | 1.8 | 1800 | 2.5 | 2500 | 8.2021 | 7.38 | 79.4088 | 651.3189 | 77 | 55 | 10 | D | 1 | 2 | 1.2 | 0 | 30 | 325.5761 | EU-4 | NA | EU-4 | EU-7 | HEPA | 451.7047 | 451.7047 | 15 | 336 | 0 | 0 | 0 | 787.7047 |  | DX | HEATER |  | 0.94267 | 0.72223 |  |  |  | 1 |  |  | 2
14 | AHU-03 |  | Clean Utensil | 2.8 | 2800 | 2.25 | 2250 | 2.5 | 2500 | 8.2021 | 6.3 | 67.788 | 556.0039 | 77 | 55 | 40 | D | 1 | 0 | 1.2 | 0 | 30 | 277.9308 | EU-4 | NA | EU-4 | EU-7 | HEPA | 111.0577 | 277.9308 | 15 | 0 | 230 | 0 | 0 | 47.9308 |  | DX | HEATER |  | 0.299 | 0.6784 |  |  |  | 1 |  |  | 2
[23 empty] | 954.2291 | [5 empty] | 736.7486 | 1080.3577 | 60 |  |  |  |  | 1186.3577 | 166 |  |  | 1200 | 1.7487 | 2.5687
15 | AHU-5B |  | Secondary packing 01 | 10.2 | 10200 | 5 | 5000 | 2.5 | 2500 | 8.2021 | 51 | 548.76 | 4500.9843 | 77 | 55 | 0 | CNC | 15 | 5 | 1.2 | 0 | 20 | 1500.3281 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 2039.2951 | 2039.2951 | 225 | 0 | 225 | 0 | 0 | 1814.2951 |  | DX | HEATER |  | 5.1906 | 8.4107 | [6 empty] | 6 |  |  | 6
[23 empty] | 1500.3281 | [5 empty] | 2039.2951 | 2039.2951 | 225 |  |  |  |  | 1814.2951 | 0 |  |  | 3000 | 5.1906 | 8.4107
16 | AHU-5A |  | Secondary packing 02 | 10.2 | 10200 | 5 | 5000 | 2.5 | 2500 | 8.2021 | 51 | 548.76 | 4500.9843 | 77 | 55 | 0 | CNC | 15 | 5 | 1.2 | 0 | 20 | 1500.3281 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 2039.2951 | 2039.2951 | 225 | 0 | 225 |  |  | 1814.2951 |  | DX | HEATER |  | 5.1906 | 8.4107 | [6 empty] | 6 |  |  | 6
[23 empty] | 1500.3281 | [5 empty] | 2039.2951 | 2039.2951 | 225 |  |  |  |  | 1814.2951 | 0 |  |  | 3000 | 5.1906 | 8.4107
17 | AHU-5C |  | Secondary packing 03 | 13.4 | 13400 | 5 | 5000 | 2.5 | 2500 | 8.2021 | 67 | 720.92 | 5913.0577 | 77 | 55 | 0 | CNC | 15 | 5 | 1.2 | 0 | 20 | 1971.0192 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 2204.9014 | 2204.9014 | 225 | 0 | 225 | 0 | 0 | 1979.9014 |  | DX | HEATER |  | 5.5035 | 9.06 | [6 empty] | 8 |  |  | 8
[23 empty] | 1971.0192 | [5 empty] | 2204.9014 | 2204.9014 | 225 |  |  |  |  | 1979.9014 | 0 |  |  | 3000 | 5.5035 | 9.06
18 | AHU-05 |  | 2.0 mtr Wide Corridor | 33.6 | 33600 | 2 | 2000 | 2.5 | 2500 | 8.2021 | 67.2 | 723.072 | 5930.7087 | 77 | 55 | 0 | CNC | 2 | 0 | 1.2 | 0 | 20 | 1976.9029 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 916.7079 | 916.7079 | 60 | 0 | 0 | 0 | 0 | 916.7079 |  | DX | HEATER |  | 2.1686 | 5.512 | [9 empty] | 4 |  |  | 5
19 | AHU-05 |  | Female Change Room-1 | 4 | 4000 | 2.5 | 2500 | 2.5 | 2500 | 8.2021 | 10 | 107.6 | 882.5459 | 77 | 55 | 0 | CNC | 5 | 0 | 1.2 | 0 | 20 | 294.182 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 332.7551 | 332.7551 | 60 | 0 | 100 | 0 | 0 | 232.7551 |  | DX | HEATER |  | 1.0745 | 2.5195 | [10 empty] | 2 |  |  | 2
20 | AHU-05 |  | Female Change Room-2 | 4 | 4000 | 2.5 | 2500 | 2.5 | 2500 | 8.2021 | 10 | 107.6 | 882.5459 | 77 | 55 | 0 | CNC | 5 | 0 | 1.2 | 0 | 20 | 294.182 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 332.7551 | 332.7551 | 60 | 0 | 0 | 0 | 0 | 332.7551 |  | DX | HEATER |  | 1.0745 | 2.5195 | [10 empty] | 2 |  |  | 2
21 | AHU-05 |  | Male Change Room-1 | 3 | 3000 | 3 | 3000 | 2.5 | 2500 | 8.2021 | 9 | 96.84 | 794.2913 | 77 | 55 | 0 | CNC | 5 | 0 | 1.2 | 0 | 20 | 264.7638 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 322.4047 | 322.4047 | 60 | 0 | 100 | 0 | 0 | 222.4047 |  | DX | HEATER |  | 1.0549 | 2.4789 | [10 empty] | 2 |  |  | 2
22 | AHU-05 |  | Male Change Room-2 | 3 | 3000 | 3 | 3000 | 2.5 | 2500 | 8.2021 | 9 | 96.84 | 794.2913 | 77 | 55 | 0 | CNC | 5 | 0 | 1.2 | 0 | 20 | 264.7638 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 181.3178 | 181.3178 | 60 | 0 | 0 | 0 | 0 | 181.3178 |  | DX | HEATER |  | 0.50705 | 0.36523 | [10 empty] | 2 |  |  | 2
23 | AHU-05 |  | Buffer Airlock | 2 | 2000 | 3 | 3000 | 3 | 3000 | 9.8425 | 6 | 64.56 | 635.4331 | 77 | 55 | 0 | CNC | 1 | 0 | 1.2 | 0 | 20 | 211.811 | EU-4 | NA | EU-4 | EU-7 | DIFFUSER | 151.2193 | 151.2193 | 15 | 0 | 115 | 0 | 0 | 36.2193 |  | DX | HEATER |  | 0.46115 | 1.3144 | [10 empty] | 1 |  |  | 1
[23 empty] | 3306.6054 | [5 empty] | 2237.16 | 2237.16 | 315 |  |  |  |  | 1922.16 | 0 |  |  | 3000 | 6.3407 | 14.7096
24 | EXT-1 |  | Electrical room | 3 | 3000 | 6.2 | 6200 | 3.5 | 3500 | 11.4829 | 18.6 | 200.136 | 2298.1496 | 77 | 55 | 0 | NC | 1 | 0 | 1.2 | 0 | 30 | 1149.0748 | NA | NA | NA | NA | NA | [32 empty] | 1
25 | EXT-2 |  | Gents Toilet | 3 | 3000 | 4.3 | 4300 | 2.5 | 2500 | 8.2021 | 12.9 | 138.804 | 1138.4843 | 77 | 55 | 0 | NC | 2 | 0 | 1.2 | 0 | 30 | 569.2421 | NA | NA | NA | NA | NA | [29 empty] | 2 |  |  | 2
26 | EXT-3 |  | Ledies Toilet | 3 | 3000 | 4.5 | 4500 | 2.5 | 2500 | 8.2021 | 13.5 | 145.26 | 1191.437 | 77 | 55 | 0 | NC | 2 | 0 | 1.2 | 0 | 30 | 595.7185 | NA | NA | NA | NA | NA | [29 empty] | 2 |  |  | 2
[45 empty] | 6 | 8 | 7 | 0 | 38 | 10 | 0 | 24 | 9 |  | 5 | 9 | 0 | 4 | 0 | 0 | 5 | 0
Note on AL15: SMB: INCREASE AHU CFM INSTEAD OF FRESH AIR FOR BALANCING
Note on AL23: SMB: INCREASE AHU CFM FOR FRESH AIR COMPANSATE